# 78ET-1

# Sr. No. 5

# EXAMINATION OF MARINE ENGINEER OFFICER

ELECTRO TECHNOLOGY

### CLASS I

(Time allowed - 3 hours)

INDIA (2001)                                                                              Morning Paper           	                             Total Marks  100

N.B. -        (1) Attempt  SIX questions only, with a minimum of TWO Questions from each Part.

(2) All questions carry equal marks.

(3) Neatness in handwriting and clarity in expression carries weightage

##### Part A

- Find the no-load terminal voltage of a four-pole, star- connected, marine, turbo-alternator from the following data: Flux per pole (assumed sinusoidally distributed) 0.12 Wb; slots per pole per phase 4, conductors per slot 4, coil-span 150O, connection-star, speed 1500 rev/min.

- A 75kW, 440V, three-phase, wound-rotor induction motor has a rotor resistance and standstill reactance of 0.02 and 0.27(/ph respectively. The stator to rotor phase turns ratio is 3.1 and the stator windings are connected in delta. If the motor is started by means of a resistance starter having a resistance of 0.25 52/ph, calculate the current taken by the motor from the supply,

- at starting,

- under full-load running conditions if the full-load slip is 4 per cent.

What would be the current taken from the supply if the motor was accidentally started with the starting resistance in the “run” position? Neglect the no-load current and the resistance and reactance of the stator windings. Assume the rotor to be star-connected.

- A 14.92kW, 440V, three-phase star-connected synchronous motor has an armature of which the effective resistance per phase is 0.4(. It is giving its full-load output at a leading power factor of 0.9. If the iron and friction losses amount to 500W, find the armature current.

- From the output characteristic shown in figure given below, deduce the transfer characteristic, and hence find the current gain for the transistor when connected in the common or grounded-emitter mode.

- A coil of unknown inductance and resistance is connected in series with a 25(, non-inductive resistor across 250V, 50Hz mains. The p.d. across the resistor is found to be 150V and across the coil 180V. Calculate the value of coil resistance and induc- tance. Find also the power factor of the coil.

- A single-phase synchronous motor generates a back e.m.f. of 250 volts, lagging by 210O behind the applied e.m.f. of 200 volts. The armature synchronous reactance is 2.5 times its resistance. What power-factor is the motor operating on, and does the current lag or lead?

##### Part B

- Write notes on the following:

- transistors,

- capacitors,

- inductors.

- Why is plain overload protection insufficient in the case of large alternator?

- Explain what steps are taken to ensure that an alternator shall generate an e.m.f., the wave form of which shall be a close approximation to a sine wave.

- (a) Sketch a direct on line starter suitable for a three phase a.c. induction motor.

(b) Explain the limitations of the direct on line starter with respect to length of starting time and repeated successive starts.

-----------------------------X-----------------------

# 78ET-1

# Sr. No. 5

# EXAMINATION OF MARINE ENGINEER OFFICER

ELECTRO TECHNOLOGY

### CLASS I

(Time allowed - 3 hours)

INDIA (2001)                                                                              Morning Paper           	                             Total Marks  100

N.B. -        (1) Attempt  SIX questions only, with a minimum of TWO Questions from each Part.

(2) All questions carry equal marks.

(3) Neatness in handwriting and clarity in expression carries weightage

##### Part A

## Answers

Answer for Question No. 1

Ans.	Distribution Factor KD =    sin n(/2

n sin (/2

=   sin  4 ( 15/2

4 sin 15/2

Note ( =    180   =   180    = 15O

3 ( n       3 ( 4

So KD = sin 30  =          0.5       =      0.5     = 0.958

4 sin 7.5    4 ( 0.1305       0.522

Pitch Factor KS = cos (/2 where ( = 180 - 150 = 30O

or KS = cos 30/2  = cos 15 = 0.966

Generated Voltage per phase or Eph = 2.22 KDKSZph(f

Here f  = 4 ( 1500 = 50Hz

120

(Eph = 2.22 ( 0.958 ( 0.966 ( (4 ( 4 ( 4) ( 0.12 ( 50

= 2.22 ( 0.958 ( 0.966 ( 64 ( 6 = 789V

Terminal Voltage = (3 ( 789 = 1367V or 1.367kV.

Answer for Question No. 2

Ans.

- Stator phase voltage = 440V

Due to transformer action, the rotor-phase voltage = 440 = 146V

3

At standstill rotor resistance per phase = 0.02( and the starter resistance per phase = 0.25(

Total rotor standstill resistance per phase = 0.02 + 0.25 = 0.27(

Rotor standstill reactance per phase = 0.27(

Total rotor circuit standstill impedance = (272 + (272 = (0.1458 = 0.382(

Rotor current per phase at standstill =146.7 = 384 A

0.382

By transformer action, stator current per phase = 384 = 128A

3

(Line current taken from the supply at starting = (3 ( 128 = 229A

- Under running conditions, the starting resistance is cut out and the slip is 4 per cent.

( Rotor-phase voltage = slip ( standstill phase voltage = 0.04 ( 146.7 = 5.87V

Rotor reactance per phase = slip ( sstandstill reactance = 0.04 ( 0.27 = 0.0108(

Rotor impedance pet phase = (0.022 + 0.01082  = (0.0004 + 0.000117

= (0.000517 = 0.0227 2

Rotor current per phase = 5.87 = 259A

0.0227

By transformer action, stator currents per phase = 259 = 86.6A

3

Line current taken from the supply = (3 ( 86.3 = 149.5A

At starting, with resistance cut out, rotor impedance per phase = (0.022 + 0.0729

= (0.0004 + 0.0729

= (0.0733 = 0.271(

Rotor current per phase = 146.7 = 541A

0.271

By transformer action, the stator currents per phase = 541    = 180.3A

3

and the line current taken from the supply = (3 ( 180.3 = 1.732 ( 180.3 = 312A

Note. The power rating given in the question is superfluous information.

Answer for Question No. 3

Ans.	Electrical output of motor = (20 ( 746) + 500 = 14920 + 500 = 15420W

Also since output P = (3 VI cos ( - 3 I2Rph

we have 3 I2 Rph - (3 VI cos ( + P = 0

or I = (3 V cos ( ( (((3 V cos ()2 - (4 ( 3 Rph P)

2 ( 3 Rph

= (3 ( 440 ( 0.9 ± (3(440 ( 0.9)2 - (12 ( 0.4 ( 15420)

6 ( 0.4

= (3 ( 396 ±  (3 ( 3962 - (12 ( 6168)

2.4

= 686  ± (470448 - 74016 = 686  ± (396432

2.4                            2.4

= 686 ± 102(39.64 = 686 ± (102 ( 6.3)

2.4                         2.4

= 686  - 630 = 56 = 23.3A.

  - 2.4

Answer for Question No. 4

Ans.	For a constant Vc of -4.5 volts, the following values can be read off from figure given above.

| Ib (microamperes) | 20 | 40 | 60 | 80 | 100 | 120 | 140 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Ic (milliamperes) | 1.2 | 2.3 | 3.4 | 4.5 | 5.6 | 6.7 | 8 |

When the above results are plotted the following can be deduced from the transfer characteristic.

( = (Ic = (5.6 - 2.3)10-3  = 3.3 ( 103 = 330

(Ib    (100 - 40)10-6          60           6

Thus current gain = 55.

#### Answer for Question No. 5

Ans.

From the diagram of the following mathematical solution is possible.

Let x = the resistive voltage drop of the coil

y = the reactive voltage drop of the coil

Then x2 + y2 = 1802 -------- (a)

And (x + 150)2 + y2 -------- (b)

Or, on further simplification and rearranging of (b) and (a), we have

x2 + 300x + 1502 + y2 = 2502 and x2 + y2 = 1802

Then by subtraction 300x + 1502 = 2502 – 1802

or 300x = (250 + 180) (250 - 180) – 1502

giving 300x = 430 ( 70 – 1502 = 7600 or x = 76/3 = 25.33V

Then y2 = 1802 - 25.332 = 32400 – 641.6 = 31758.4

Or  y = 102(3.176 = 178.2V The circuit current = 150/25 = 6A

Resistance of coil = 25.33/6 = 4.221(

Reactance of coil = 178.2/6 = 29.7

Inductance of coil = 29.7/2 ( 3.14 ( 50 = 0.0945H

Power factor of coil cos (L = 25.33/180 = 0. 141 (lagging).

#### Answer for Question No. 6

Ans. 0.88pf leading