# 78ET-1

# Sr. No. 7

# EXAMINATION OF MARINE ENGINEER OFFICER

ELECTRO TECHNOLOGY

### CLASS I

(Time allowed - 3 hours)

INDIA (2001)                                                                              Morning Paper           	                             Total Marks  100

N.B. -        (1) Attempt  SIX questions only, with a minimum of TWO Questions from each Part.

(2) All questions carry equal marks.

(3) Neatness in handwriting and clarity in expression carries weightage

PART A

- The terminal voltage of a three-phase alternator is set at 440V, by adjusting the field excitation when the speed is correct and when the full-load current is supplied at a power factor of 0.8 (lagging). When the machine circuit breaker is opened and the load thrown-off, the terminal voltage is seen to rise to 506V. Estimate the voltage regulation.

- A 37kW, twelve-pole, three-phase, 50Hz squirrel-cage induction motor as used aboard a tank-ship for driving a main circulating water pump, gave the following test results

No load Test.

Applied voltage 440V. Line current 19A. Input power 2.17kW

Locked-rotor Test.

Applied voltage 100V. Line current 70A. Input power 3.88kW.

The ratio stator/rotor copper loss is 4: 5. Construct a circle diagram and find for full-load conditions

- Input line-current and power factor,

- percentage slip,

- percentage efficiency.

- Find the ratio of starting to full-load current for a 15kW, 415V, three-phase, induction motor with a star-delta starter, given that the full-load efficiency is 85 per cent, the full-load power factor is 0.8 (lagging), the short-circuit current is 60A at 220V and the magnetising current is negligible.

- The data given in the table refers to a p-n-p transistor in the common-emitter configuration.

| Collector Voltage VC (volts) | Collector Current IC (milli-amperes) |
| --- | --- |
|  | Base Current Ib = -20mA | Base Current Ib = -40mA | Base Current Ib = -60mA | Base Current Ib = -80mA |
| - 3 | - 0.91 | - 1.6 | - 2.3 | - 3.0 |
| - 5 | - 0.93 | - 1.7 | - 2.5 | - 3.25 |
| - 7 | - 0.97 | - 1.85 | - 2.7 | - 3.55 |
| - 9 | - 1.0 | - 2.05 | - 3.0 | - 4.05 |

Plot the collector current/collector voltage characteristic for base currents of -20, -40, -60 and –80 (A and using these determine

- the output resistance of the transistor for the Ib = -60(A condition, and

- the current gain when the collector voltage is -6V.

- With reference to "p" and "n" type germanium crystals explain the meaning of three of the following terms

- donorion,

- acceptor ion,

- valency electrons,

- co-valent bonds.

- Whilst in port a tank-ship obtained its “shore-main” supply from a three-phase, 3300/440V, delta-star transformer. For fighting purposes on board ship the voltage is stepped down by three, 440/110V, single-phase transformers connected in delta/delta. If the total lighting load, comprised of tungsten filament and fluorescent lamps, is balanced to 15kW at a power factor of 0.85 (lagging), calculate the currents in the respective connecting cables and the phase currents of the transformer windings. What would be the kVA supplied from the high-voltage supply? It is assumed that the transformer losses are negligible and only the lighting is being supplied.

PART  B

- (a) Describe fully one method of determining the efficiency of a large turbo-alternator.

(b) Why is plain overload protection insufficient in the case of large alternator?

- Draw the equivalent circuits for a single-phase transformer, explaining the significance of each portion of the circuits. Construct a vector diagram, comparing it step by step with the equivalent circuits diagram.

- With reference to electrical switch gear explain the purpose of each of the following:

(a) Preferential tripping,

(b) Dash pots.

(c) Reverse power tripping;

(d) Under voltage tripping.

- With the aid of sketches, describe operation of -

- a thermal type single phasing preventer for a three phase induction motor; and

- A magnetic overload element, incorporating a time delay device.

------------------------X-------------------

# 78ET-1

# Sr. No. 7

# EXAMINATION OF MARINE ENGINEER OFFICER

ELECTRO TECHNOLOGY

### CLASS I

(Time allowed - 3 hours)

INDIA (2001)                                                                              Morning Paper           	                             Total Marks  100

N.B. -        (1) Attempt  SIX questions only, with a minimum of TWO Questions from each Part.

(2) All questions carry equal marks.

(3) Neatness in handwriting and clarity in expression carries weightage

##### Part A

## Answers

#### Answer for Question No. 1

Ans. 	Voltage regulation = 506 – 440   ( 100

440

=   66   (   100 =   66    =   6

440                    4.4       0.4

= 15 per cent (up).

Answer for Question No. 2

Ans.	Power factor of no-load current =       2170        = 0.13

(3 ( 440 ( 19

With full voltage applied to results of locked rotor test,

Standstill current =440 ( 70 = 308A

100

Power factor of this S.C. current =        3880      = 0.32 (lagging)

(3 ( 100 ( 70

Current scale - 10mm = 20A (This was for the original diagram before photographic reduction.)

( Length of no-load current phasor = 9.5 mm

Length of standstill current phasor = 154 mm

Power component of output = 50 ( 746 = 49A

(3 ( 440

This is represented by a vertical phasor from the output line

= 49 = 24.5 mm

20

On the circle diagram shown, line XY is drawn parallel to the output line BAS, spaced 24.5 cm The point of intersection with the circle is A. ( Input line current OA = 31mm = 62A. Power factor = 0.89 (from the power-factor quadrant).

Efficiency = Output = AK (mm) = 25 = 0.8928 = 89.3 per cent.

Input      AL (mm)    28

Note. The copper losses have been divided in the ratio 4: 5 by the simple geometrical construction shows that DW is divided into nine parts and the appropriate parallel drawn to give point C.

Slip = KJ  =  10 mm    = 0.0385 = 3.85 per cent.

AJ      260 mm

Answer for Question No. 3

Ans.	Full-load current of motor =	15000                   = 30.5A

(3 ( 415 ( 0.8 ( 0.85

With the starter in "star" position, the voltage per phase = 415 = 240V

(3

With the motor connected in "delta" and an applied voltage of 220V,

the current per phase = 60 amperes

(3

The current under starting conditions, with 415 volts applied across each phase,

(3

would be 60 ( 415  (   1   =  6 ( 415 = 415 = 37.7A

(3     (3        220        3 ( 22       11

Ratio of starting current to fuU4oad current is given by Starting current   = 37.7 = 1.24

Full-load current      30.5

Answer for Question No. 4

Ans.	Overleaf is shown the required output characteristic of a transistor connected in the common-emitter mode.

Then (a) Output Resistance r0 = (Vc

(Ic

Considering the 60(A characteristic we have

(Vc =      (7 - 5)      = 2 ( 103

(Ic      (2.7 - 2.5)10-3      0.2

Thus r0' = 10000 ohms or 10k(

Also (b) Current Gain ( = (Ic

(Ib

For a collector voltage of - 6V

(Ic = AB = (3.4 - 0-95)10-3 = 2.45 ( 10-3 amperes

(Ib = 80 - 20 = 60 ( 10-6 = 60 ( 10-6 amperes

So ( = (Ic = 2.45 ( 10-3 = 2.45 ( 103 = 245 = 40.8

(Ib       60 ( 10-6	      60           6

Thus ( = 41.

The current gain value can also be obtained from the transfer characteristic, which can be deduced as shown below. The 3, 5 and 7 V graphs are drawn and the 6V line deduced-shown dotted.

Then ( = (Ic  = (3 - 1) 10-3 =        2       = 2000 = 40.

(Ib      (70-20)10-6    50 ( 10-3      50

Answer for Question No. 6

Ans. 	lighting transformer.

Secondary line current =           15000          = 93A

(3 ( 110 ( 0.85

Secondary phase current =  93   = 54A

(3

Primary phase current = 54 ( 110 = 13.5A

440

Primary line current = 13.5 ( (3 = 23.3A

Supply transformer.

Secondary line current = 23.3A

Secondary phase current = 23.3A (since the windings are connected in star)

Primary phase current = 23.3 ( 440/(3 = 1.76A

3300

Primary line current = 1.8 ( (3 = 3.1A

Assuming no losses

kVA input from supply = kVA output from lighting transformer

=   kW    =   15   = 17.65kVA.

cos (      0.85